## Settings
| Generator Data |  | For Testing
| Voltage (kV, line-to-line) | 11
| Power (MVA) | 15.829
| PT Ratio | 167
| CT Ratio | 3600
| Xd (pu) | 118
| X'd (pu) | 20
| ZB (ohms secondary) | 164.7851
Settings
VNOM (volts secondary)
INOM (amps secondary)
Zone 1
| Z1 Diameter (ohms secondary) | 114.7
| Z1 Offset (ohms secondary) | -12.6
| Z1 Trip time (sec) | 0.5
Zone 2
| Z2 Diameter (ohms secondary) | 149.1
| Z2 Offset (ohms secondary) | -12.6
| Z2 Trip time (sec) | 3
Omicron Settings Zone 1
| ¦Z¦ (ohms) | 69.95
| Phi (degrees) | 270
| Radius (Ohms) | 57.35
| Start Angle (degrees) | 360
| End angle (degrees) | 0
Omicron Settings Zone 2
| ¦Z¦ (ohms) | 87.15
| Phi (degrees) | 270
| Radius (Ohms) | 74.55
| Start Angle (degrees) | 360
| End angle (degrees) | 0
This is for calculating the relay settings |  |  | For calculating settings
Generator Data
| Voltage (kV, line-to-line) | 20
| Power (MVA) | 492
| PT Ratio | 167
| CT Ratio | 3600
| Xd (pu) | 1.1888
| X'd (pu) | 0.20577
| ZB (ohms secondary) | 17.5259
Settings
| VNOM (volts secondary) | 119.7605
| INOM (amps secondary) | 3.9452
Zone 1
| Z1 Diameter (ohms secondary) | 17.5259
| Z1 Offset (ohms secondary) | -1.8032
| Z1 Trip time (sec) | 0.1
Zone 2
| Z2 Diameter (ohms secondary) | 20.8348
| Z2 Offset (ohms secondary) | -1.8032
| Z2 Trip time (sec) | 0.5
Omicron Settings Zone 1
| ¦Z¦ (ohms) | 10.5661
| Phi (degrees) | 270
| Radius (Ohms) | 8.763
| Start Angle (degrees) | 360
| End angle (degrees) | 0
Omicron Settings Zone 2
| ¦Z¦ (ohms) | 12.2206
| Phi (degrees) | 270
| Radius (Ohms) | 10.4174
| Start Angle (degrees) | 360
| End angle (degrees) | 0

## Curve
Mho Element - Zone 1 |  |  | Mho Element - Zone 2 |  |  | Mho Element - Zone 1 |  |  | Mho Element - Zone 2
Angle (degrees) | R (ohms) | X (ohms) | Angle (degrees) | R (ohms) | X (ohms) | Angle (degrees) | R (ohms) | X (ohms) | Angle (degrees) | R (ohms) | X (ohms)
0 | 57.35 | -69.95 | 0 | 74.55 | -87.15 | 0 | 8.763 | -10.5661 | 0 | 10.4174 | -12.2206
10 | 56.4787 | -59.9913 | 10 | 73.4174 | -74.2045 | 10 | 8.6298 | -9.0444 | 10 | 10.2591 | -10.4116
20 | 53.8914 | -50.3351 | 20 | 70.0541 | -61.6524 | 20 | 8.2345 | -7.569 | 20 | 9.7892 | -8.6576
30 | 49.6666 | -41.275 | 30 | 64.5622 | -49.875 | 30 | 7.5889 | -6.1846 | 30 | 9.0217 | -7.0119
40 | 43.9326 | -33.0861 | 40 | 57.1086 | -39.2302 | 40 | 6.7128 | -4.9334 | 40 | 7.9802 | -5.5244
50 | 36.8639 | -26.0174 | 50 | 47.9198 | -30.0414 | 50 | 5.6327 | -3.8533 | 50 | 6.6962 | -4.2404
60 | 28.675 | -20.2834 | 60 | 37.275 | -22.5878 | 60 | 4.3815 | -2.9772 | 60 | 5.2087 | -3.1988
70 | 19.6149 | -16.0586 | 70 | 25.4976 | -17.0959 | 70 | 2.9971 | -2.3316 | 70 | 3.563 | -2.4314
80 | 9.9587 | -13.4713 | 80 | 12.9455 | -13.7326 | 80 | 1.5217 | -1.9363 | 80 | 1.809 | -1.9614
90 | 7.0262e-15 | -12.6 | 90 | 9.1335e-15 | -12.6 | 90 | 1.0736e-15 | -1.8032 | 90 | 1.2763e-15 | -1.8032
100 | -9.9587 | -13.4713 | 100 | -12.9455 | -13.7326 | 100 | -1.5217 | -1.9363 | 100 | -1.809 | -1.9614
110 | -19.6149 | -16.0586 | 110 | -25.4976 | -17.0959 | 110 | -2.9971 | -2.3316 | 110 | -3.563 | -2.4314
120 | -28.675 | -20.2834 | 120 | -37.275 | -22.5878 | 120 | -4.3815 | -2.9772 | 120 | -5.2087 | -3.1988
130 | -36.8639 | -26.0174 | 130 | -47.9198 | -30.0414 | 130 | -5.6327 | -3.8533 | 130 | -6.6962 | -4.2404
140 | -43.9326 | -33.0861 | 140 | -57.1086 | -39.2302 | 140 | -6.7128 | -4.9334 | 140 | -7.9802 | -5.5244
150 | -49.6666 | -41.275 | 150 | -64.5622 | -49.875 | 150 | -7.5889 | -6.1846 | 150 | -9.0217 | -7.0119
160 | -53.8914 | -50.3351 | 160 | -70.0541 | -61.6524 | 160 | -8.2345 | -7.569 | 160 | -9.7892 | -8.6576
170 | -56.4787 | -59.9913 | 170 | -73.4174 | -74.2045 | 170 | -8.6298 | -9.0444 | 170 | -10.2591 | -10.4116
180 | -57.35 | -69.95 | 180 | -74.55 | -87.15 | 180 | -8.763 | -10.5661 | 180 | -10.4174 | -12.2206
190 | -56.4787 | -79.9087 | 190 | -73.4174 | -100.0955 | 190 | -8.6298 | -12.0878 | 190 | -10.2591 | -14.0295
200 | -53.8914 | -89.5649 | 200 | -70.0541 | -112.6476 | 200 | -8.2345 | -13.5632 | 200 | -9.7892 | -15.7835
210 | -49.6666 | -98.625 | 210 | -64.5622 | -124.425 | 210 | -7.5889 | -14.9476 | 210 | -9.0217 | -17.4293
220 | -43.9326 | -106.8139 | 220 | -57.1086 | -135.0698 | 220 | -6.7128 | -16.1988 | 220 | -7.9802 | -18.9167
230 | -36.8639 | -113.8826 | 230 | -47.9198 | -144.2586 | 230 | -5.6327 | -17.2789 | 230 | -6.6962 | -20.2008
240 | -28.675 | -119.6166 | 240 | -37.275 | -151.7122 | 240 | -4.3815 | -18.1551 | 240 | -5.2087 | -21.2423
250 | -19.6149 | -123.8414 | 250 | -25.4976 | -157.2041 | 250 | -2.9971 | -18.8006 | 250 | -3.563 | -22.0097
260 | -9.9587 | -126.4287 | 260 | -12.9455 | -160.5674 | 260 | -1.5217 | -19.1959 | 260 | -1.809 | -22.4797
270 | -7.0262e-15 | -127.3 | 270 | -9.1335e-15 | -161.7 | 270 | -1.0736e-15 | -19.3291 | 270 | -1.2763e-15 | -22.638
280 | 9.9587 | -126.4287 | 280 | 12.9455 | -160.5674 | 280 | 1.5217 | -19.1959 | 280 | 1.809 | -22.4797
290 | 19.6149 | -123.8414 | 290 | 25.4976 | -157.2041 | 290 | 2.9971 | -18.8006 | 290 | 3.563 | -22.0097
300 | 28.675 | -119.6166 | 300 | 37.275 | -151.7122 | 300 | 4.3815 | -18.1551 | 300 | 5.2087 | -21.2423
310 | 36.8639 | -113.8826 | 310 | 47.9198 | -144.2586 | 310 | 5.6327 | -17.2789 | 310 | 6.6962 | -20.2008
320 | 43.9326 | -106.8139 | 320 | 57.1086 | -135.0698 | 320 | 6.7128 | -16.1988 | 320 | 7.9802 | -18.9167
330 | 49.6666 | -98.625 | 330 | 64.5622 | -124.425 | 330 | 7.5889 | -14.9476 | 330 | 9.0217 | -17.4293
340 | 53.8914 | -89.5649 | 340 | 70.0541 | -112.6476 | 340 | 8.2345 | -13.5632 | 340 | 9.7892 | -15.7835
350 | 56.4787 | -79.9087 | 350 | 73.4174 | -100.0955 | 350 | 8.6298 | -12.0878 | 350 | 10.2591 | -14.0295
360 | 57.35 | -69.95 | 360 | 74.55 | -87.15 | 360 | 8.763 | -10.5661 | 360 | 10.4174 | -12.2206